## Thoreau
Concord School system - Thoreau
Lighting Worksheet
Auditor: Barney Judge
| SITE LOCATION | Flr | EXISTING | PRODUCT | QTY | E-Watts | Total | RUN | kWh | ANNUAL COST | PROPOSED | QTY | Sensor | QTY | DEVICE | P-watts | StepDim | Prop | TOT | kWh | % Sen | % Power | KWH | Total | ANNUAL COST | Annual
Sort |  |  |  | CODE |  |  | KW | HRS | Pre | 0.166 |  |  | Type |  | CODE |  | 50%/Watts | RunHRS | KW | Post | saving | StepDim | SvDim | Post-KWH | (PROPOSED) | CostSving
| SITE LOCATION |  |  | E-Code | [6 empty] | PROPOSED | QTY |  |  | P-code
1 | KITCHEN | 1 | TT/2FB32/E | 2F32SSE | 12 | 60 | 0.72 | 3200 | 2304 | 382.464 | RB/TT/22W_2BAR/_KIT | 12 |  |  | 1L020 | 22 | 0 | 3200 | 0.264 | 844.8 | 0% | 0% | 0 | 844.8 | 140.2368 | 242.2272
2 | RESTROOMS | 1 | RC6/2X18W/CFL | 2C0018E | 2 | 40 | 0.08 | 3200 | 256 | 42.496 | NEW/13W/LED/RECESSED CAN | 2 |  |  | 1L013 | 13 | 0 | 3200 | 0.026 | 83.2 | 0% | 0% | 0 | 83.2 | 13.8112 | 28.6848
3 | RESTROOMS | 1 | RC6/2X18W/CFL | 2C0018E | 2 | 40 | 0.08 | 3200 | 256 | 42.496 | NEW/13W/LED/RECESSED CAN | 2 |  |  | 1L013 | 13 | 0 | 3200 | 0.026 | 83.2 | 0% | 0% | 0 | 83.2 | 13.8112 | 28.6848
4 | KITCHEN | 1 | RC6/2X18W/CFL | 2C0018E | 6 | 40 | 0.24 | 3200 | 768 | 127.488 | NEW/13W/LED/RECESSED CAN | 6 |  |  | 1L013 | 13 | 0 | 3200 | 0.078 | 249.6 | 0% | 0% | 0 | 249.6 | 41.4336 | 86.0544
5 | CAFÉ | 1 | PEND/250W/MH/GLOBE | 1M0250S | 16 | 295 | 4.72 | 3200 | 15104 | 2507.264 | NA | 0 |  |  | NA | 295 | 0 | 3200 | 4.72 | 15104 | 0% | 0% | 0 | 15104 | 2507.264 | 0
6 | CAFÉ | 1 | WALL/42W/CFL/GLOBE | 1C0042E | 7 | 48 | 0.336 | 3200 | 1075.2 | 178.4832 | NA | 0 |  |  | NA | 48 | 0 | 3200 | 0.336 | 1075.2 | 0% | 0% | 0 | 1075.2 | 178.4832 | 0
7 | CAFÉ | 1 | RC6/2X18W/CFL | 2C0018E | 14 | 40 | 0.56 | 3200 | 1792 | 297.472 | NEW/13W/LED/RECESSED CAN | 14 |  |  | 1L013 | 13 | 0 | 3200 | 0.182 | 582.4 | 0% | 0% | 0 | 582.4 | 96.6784 | 200.7936
8 | CAFÉ | 1 | RC6/2X18W/CFL | 2C0018E | 1 | 40 | 0.04 | 3200 | 128 | 21.248 | NEW/13W/LED/RECESSED CAN | 1 |  |  | 1L013 | 13 | 0 | 3200 | 0.013 | 41.6 | 0% | 0% | 0 | 41.6 | 6.9056 | 14.3424
9 | CAFÉ MENS RM | 1 | RC6/2X18W/CFL | 2C0018E | 3 | 40 | 0.12 | 3200 | 384 | 63.744 | NEW/13W/LED/RECESSED CAN | 3 |  |  | 1L013 | 13 | 0 | 3200 | 0.039 | 124.8 | 0% | 0% | 0 | 124.8 | 20.7168 | 43.0272
10 | CAFÉ WOMENS RM | 1 | RC6/2X18W/CFL | 2C0018E | 3 | 40 | 0.12 | 3200 | 384 | 63.744 | NEW/13W/LED/RECESSED CAN | 3 |  |  | 1L013 | 13 | 0 | 3200 | 0.039 | 124.8 | 0% | 0% | 0 | 124.8 | 20.7168 | 43.0272
11 | CAFÉ ENTRANCE | 1 | RC6/2X18W/CFL | 2C0018E | 1 | 40 | 0.04 | 3200 | 128 | 21.248 | NEW/13W/LED/RECESSED CAN | 1 |  |  | 1L013 | 13 | 0 | 3200 | 0.013 | 41.6 | 0% | 0% | 0 | 41.6 | 6.9056 | 14.3424
12 | CAFÉ ENTRANCE | 1 | RC6/2X18W/CFL | 2C0018E | 6 | 40 | 0.24 | 3200 | 768 | 127.488 | NEW/13W/LED/RECESSED CAN | 6 |  |  | 1L013 | 13 | 0 | 3200 | 0.078 | 249.6 | 0% | 0% | 0 | 249.6 | 41.4336 | 86.0544
13 | CONF RM A225 | 2 | TT/2F40/BIAX | 2F40BXE | 8 | 72 | 0.576 | 3200 | 1843.2 | 305.9712 | NEW/TT/LED/20W/ | 8 |  |  | 1L020 | 20 | 0 | 3200 | 0.16 | 512 | 0% | 0% | 0 | 512 | 84.992 | 220.9792
14 | CONF RM A225 | 2 | RC6/2X18W/CFL | 2C0018E | 1 | 40 | 0.04 | 3200 | 128 | 21.248 | NEW/13W/LED/RECESSED CAN | 1 |  |  | 1L013 | 13 | 0 | 3200 | 0.013 | 41.6 | 0% | 0% | 0 | 41.6 | 6.9056 | 14.3424
15 | DOOR 3 STAIRWELL | 1 | 16" DRUM/2X26W/CFL | 2C0026E | 4 | 54 | 0.216 | 3200 | 691.2 | 114.7392 | KIT/DRUM_18W/LED | 4 |  |  | 1L018 | 18 | 0 | 3200 | 0.072 | 230.4 | 0% | 0% | 0 | 230.4 | 38.2464 | 76.4928
16 | DOOR 3 STAIRWELL | 1 | RC6/2X18W/CFL | 2C0018E | 2 | 40 | 0.08 | 3200 | 256 | 42.496 | NEW/13W/LED/RECESSED CAN | 2 |  |  | 1L013 | 13 | 0 | 3200 | 0.026 | 83.2 | 0% | 0% | 0 | 83.2 | 13.8112 | 28.6848
17 | GYM ENT/OFC | 1 | RC6/2X18W/CFL/GLASS LENS | 2C0018E | 10 | 40 | 0.4 | 3200 | 1280 | 212.48 | NEW/13W/LED/RECESSED CAN | 10 |  |  | 1L013 | 13 | 0 | 3200 | 0.13 | 416 | 0% | 0% | 0 | 416 | 69.056 | 143.424
18 | GYM | 1 | HIGHBAY/400W/MH | 1M0400S | 16 | 455 | 7.28 | 3200 | 23296 | 3867.136 | NEW/LED/130W/SEN/STEP-DIM | 16 | integrated | 16 | 1L130 | 130 | 26 | 2400 | 2.08 | 4992 | 25% | 0% | 332.8 | 5324.8 | 883.9168 | 2983.2192
19 | TEACHER DINING A115 | 1 | TT/2F40/BIAX | 2F40BXE | 15 | 72 | 1.08 | 3200 | 3456 | 573.696 | NEW/TT/LED/20W/ | 15 |  |  | 1L020 | 20 | 0 | 3200 | 0.3 | 960 | 0% | 0% | 0 | 960 | 159.36 | 414.336
20 | RESTROOM | 1 | RC6/2X18W/CFL | 2C0018E | 1 | 40 | 0.04 | 3200 | 128 | 21.248 | NEW/13W/LED/RECESSED CAN | 1 |  |  | 1L013 | 13 | 0 | 3200 | 0.013 | 41.6 | 0% | 0% | 0 | 41.6 | 6.9056 | 14.3424
21 | THERAPY | 1 | TT/2FB31/E | 2F32SSE | 2 | 60 | 0.12 | 3200 | 384 | 63.744 | RB/TT/22W_2BAR/_KIT | 2 |  |  | 1L020 | 22 | 0 | 3200 | 0.044 | 140.8 | 0% | 0% | 0 | 140.8 | 23.3728 | 40.3712
22 | 1ST FLOOR HALL | 1 | RC6/2X18W/CFL | 2C0018E | 41 | 40 | 1.64 | 3200 | 5248 | 871.168 | NEW/13W/LED/RECESSED CAN | 41 |  |  | 1L013 | 13 | 0 | 3200 | 0.533 | 1705.6 | 0% | 0% | 0 | 1705.6 | 283.1296 | 588.0384
23 | 1ST FLOOR HALL | 1 | RC6/2X18W/CFL | 2C0018E | 16 | 40 | 0.64 | 3200 | 2048 | 339.968 | NEW/13W/LED/RECESSED CAN | 16 |  |  | 1L013 | 13 | 0 | 3200 | 0.208 | 665.6 | 0% | 0% | 0 | 665.6 | 110.4896 | 229.4784
24 | STAIRWELL 2 | 1 | 16" DRUM/2X26W/CFL | 2C0026E | 4 | 54 | 0.216 | 3200 | 691.2 | 114.7392 | KIT/DRUM_18W/LED | 4 |  |  | 1L018 | 18 | 0 | 3200 | 0.072 | 230.4 | 0% | 0% | 0 | 230.4 | 38.2464 | 76.4928
25 | 3RD FLOOR CANS | 3 | RC6/2X18W/CFL | 2C0018E | 25 | 40 | 1 | 3200 | 3200 | 531.2 | NEW/13W/LED/RECESSED CAN | 25 |  |  | 1L013 | 13 | 0 | 3200 | 0.325 | 1040 | 0% | 0% | 0 | 1040 | 172.64 | 358.56
26 | 3RD FLOOR CANS | 3 | RC6/2X18W/CFL | 2C0018E | 27 | 40 | 1.08 | 3200 | 3456 | 573.696 | NEW/13W/LED/RECESSED CAN | 27 |  |  | 1L013 | 13 | 0 | 3200 | 0.351 | 1123.2 | 0% | 0% | 0 | 1123.2 | 186.4512 | 387.2448
27 | OFFICE B320 | 3 | TT/2FB31/E/9-CELL | 2F32SSE | 4 | 60 | 0.24 | 3200 | 768 | 127.488 | RB/TT/22W_2BAR/_KIT | 4 |  |  | 1L020 | 22 | 0 | 3200 | 0.088 | 281.6 | 0% | 0% | 0 | 281.6 | 46.7456 | 80.7424
28 | OFFICE B321 | 3 | TT/2FB31/E/9-CELL | 2F32SSE | 4 | 60 | 0.24 | 3200 | 768 | 127.488 | RB/TT/22W_2BAR/_KIT | 4 |  |  | 1L020 | 22 | 0 | 3200 | 0.088 | 281.6 | 0% | 0% | 0 | 281.6 | 46.7456 | 80.7424
29 | STAIRWELL 1 | 1 | 16" DRUM/2X26W/CFL | 2C0026E | 8 | 54 | 0.432 | 3200 | 1382.4 | 229.4784 | KIT/DRUM_18W/LED | 8 |  |  | 1L018 | 18 | 0 | 3200 | 0.144 | 460.8 | 0% | 0% | 0 | 460.8 | 76.4928 | 152.9856
30 | STAIRWELL 1 | 1 | RC6/2X18W/CFL | 2C0018E | 1 | 40 | 0.04 | 3200 | 128 | 21.248 | NEW/13W/LED/RECESSED CAN | 1 |  |  | 1L013 | 13 | 0 | 3200 | 0.013 | 41.6 | 0% | 0% | 0 | 41.6 | 6.9056 | 14.3424
31 | SECOND FLR CANS | 1 | RC6/2X18W/CFL | 2C0018E | 42 | 40 | 1.68 | 2000 | 3360 | 557.76 | NEW/13W/LED/RECESSED CAN | 42 |  |  | 1L013 | 13 | 0 | 2000 | 0.546 | 1092 | 0% | 0% | 0 | 1092 | 181.272 | 376.488
32 | SECOND FLR CANS | 1 | RC6/2X18W/CFL | 2C0018E | 12 | 40 | 0.48 | 2000 | 960 | 159.36 | NEW/13W/LED/RECESSED CAN | 12 |  |  | 1L013 | 13 | 0 | 2000 | 0.156 | 312 | 0% | 0% | 0 | 312 | 51.792 | 107.568
33 | 94 WING | 2 | RC8/2X13W/CFL | 2C0013E | 6 | 28 | 0.168 | 1000 | 168 | 27.888 | NA | 0 |  |  | NA | 28 | 0 | 1000 | 0.168 | 168 | 0% | 0% | 0 | 168 | 27.888 | 0
34 | 94 WING | 2 | RC8/2X13W/CFL | 2C0013E | 8 | 28 | 0.224 | 3200 | 716.8 | 118.9888 | NA | 0 |  |  | NA | 28 | 0 | 3200 | 0.224 | 716.8 | 0% | 0% | 0 | 716.8 | 118.9888 | 0
35 | 94 WING | 2 | WALLBOX/250W/MH/UPLIGHT | 1M0250S | 7 | 295 | 2.065 | 3200 | 6608 | 1096.928 | RL/50W/LED/SCREW-IN | 7 |  |  | 1L045 | 50 | 0 | 3200 | 0.35 | 1120 | 0% | 0% | 0 | 1120 | 185.92 | 911.008
36 | ROOM B210 | 2 | TT/2FB31/E/9-CELL | 2F32SSE | 2 | 60 | 0.12 | 3200 | 384 | 63.744 | RB/TT/22W_2BAR/_KIT | 2 |  |  | 1L020 | 22 | 0 | 3200 | 0.044 | 140.8 | 0% | 0% | 0 | 140.8 | 23.3728 | 40.3712
37 | MUSIC ROOM | 2 | SAME AS ALCOTT CAFÉ | 0 | 0 | 0 | 0 | 3200 | 0 | 0 | NA | 0 |  |  | NA | 0 | 0 | 3200 | 0 | 0 | 0% | 0% | 0 | 0 | 0 | 0
38 | MUSIC ROOM | 2 | RC8/2X18W/CFL | 2C0018E | 8 | 40 | 0.32 | 3200 | 1024 | 169.984 | NA | 0 |  |  | NA | 40 | 0 | 3200 | 0.32 | 1024 | 0% | 0% | 0 | 1024 | 169.984 | 0
39 | AUDITORIUM | 1 | CYLINDER/250W/MH/PEND | 1M0250S | 11 | 295 | 3.245 | 3200 | 10384 | 1723.744 | NA | 0 |  |  | NA | 295 | 0 | 3200 | 3.245 | 10384 | 0% | 0% | 0 | 10384 | 1723.744 | 0
40 | AUDITORIUM | 1 | CYLINDER/250W/HALOGEN/PEND | 1T0250 | 22 | 250 | 5.5 | 3200 | 17600 | 2921.6 | NA | 0 |  |  | NA | 250 | 0 | 3200 | 5.5 | 17600 | 0% | 0% | 0 | 17600 | 2921.6 | 0
41 | AUDITORIUM STAGE | 1 | RC12/250W/MH | 1M0250S | 2 | 295 | 0.59 | 3200 | 1888 | 313.408 | NA | 0 |  |  | NA | 295 | 0 | 3200 | 0.59 | 1888 | 0% | 0% | 0 | 1888 | 313.408 | 0
42 | AUDITORIUM STAGE | 1 | RC8/120W/PAR38 | 1I0120 | 1 | 120 | 0.12 | 3200 | 384 | 63.744 | NA | 0 |  |  | NA | 120 | 0 | 3200 | 0.12 | 384 | 0% | 0% | 0 | 384 | 63.744 | 0
43 | LIBRARY | 1 | TT/2F40/BIAX | 2F40BXE | 22 | 72 | 1.584 | 3200 | 5068.8 | 841.4208 | NEW/TT/LED/20W/ | 22 |  |  | 1L020 | 20 | 0 | 3200 | 0.44 | 1408 | 0% | 0% | 0 | 1408 | 233.728 | 607.6928
44 | LIBRARY | 1 | RC6/2X18W/CFL | 2C0018E | 8 | 40 | 0.32 | 3200 | 1024 | 169.984 | NEW/13W/LED/RECESSED CAN | 8 |  |  | 1L013 | 13 | 0 | 3200 | 0.104 | 332.8 | 0% | 0% | 0 | 332.8 | 55.2448 | 114.7392
45 | LIBRARY | 1 | SAME AS ALCOTT CAFÉ | 0 | 12 | 0 | 0 | 3200 | 0 | 0 | NA | 0 |  |  | NA | 0 | 0 | 3200 | 0 | 0 | 0% | 0% | 0 | 0 | 0 | 0
46 | ENTRANCE HALL | 1 | TT/2F40/BIAX | 2F40BXE | 8 | 72 | 0.576 | 3200 | 1843.2 | 305.9712 | NEW/TT/LED/20W/ | 8 |  |  | 1L020 | 20 | 0 | 3200 | 0.16 | 512 | 0% | 0% | 0 | 512 | 84.992 | 220.9792
47 | ENTRANCE HALL | 1 | RC6/2X18W/CFL | 2C0018E | 4 | 40 | 0.16 | 3200 | 512 | 84.992 | NEW/13W/LED/RECESSED CAN | 4 |  |  | 1L013 | 13 | 0 | 3200 | 0.052 | 166.4 | 0% | 0% | 0 | 166.4 | 27.6224 | 57.3696
48 | OFFICE MAIN | 1 | TT/2F40/BIAX | 2F40BXE | 17 | 72 | 1.224 | 3200 | 3916.8 | 650.1888 | NEW/TT/LED/20W/ | 17 |  |  | 1L020 | 20 | 0 | 3200 | 0.34 | 1088 | 0% | 0% | 0 | 1088 | 180.608 | 469.5808
49 | OFFICE MAIN | 1 | RC6/2X18W/CFL | 2C0018E | 8 | 40 | 0.32 | 3200 | 1024 | 169.984 | NEW/13W/LED/RECESSED CAN | 8 |  |  | 1L013 | 13 | 0 | 3200 | 0.104 | 332.8 | 0% | 0% | 0 | 332.8 | 55.2448 | 114.7392
50 | NURSE'S OFC | 1 | TT/2FB31/E | 2F32SSE | 1 | 60 | 0.06 | 3200 | 192 | 31.872 | RB/TT/22W_2BAR/_KIT | 1 |  |  | 1L020 | 22 | 0 | 3200 | 0.022 | 70.4 | 0% | 0% | 0 | 70.4 | 11.6864 | 20.1856
51 | SITE LIGHTING | OUT | WP/42W/CFL/HALFMOON | 1C0042E | 21 | 48 | 1.008 | 4380 | 4415.04 | 732.8966 | KIT/DRUM_12W/LED | 21 |  |  | 1L012 | 12 | 0 | 4380 | 0.252 | 1103.76 | 0% | 0% | 0 | 1103.76 | 183.2242 | 549.6725
52 | SITE LIGHTING | OUT | SHOEBOX/150W/MH | 1M0150S | 8 | 190 | 1.52 | 4380 | 6657.6 | 1105.1616 | NEW/LED/POST-TOP/45W | 8 |  |  | 1L045 | 45 | 0 | 4380 | 0.36 | 1576.8 | 0% | 0% | 0 | 1576.8 | 261.7488 | 843.4128
53 | SITE LIGHTING | OUT | DECO/150W/MH | 1M0150S | 16 | 190 | 3.04 | 3200 | 9728 | 1614.848 | KIT/POST_TOP/LED/60W/ | 16 |  |  | 1L060 | 60 | 0 | 3200 | 0.96 | 3072 | 0% | 0% | 0 | 3072 | 509.952 | 1104.896
54 | SITE LIGHTING | OUT | RC10/100W/MH | 1M0100S | 2 | 120 | 0.24 | 3200 | 768 | 127.488 | KIT/SCREW-IN_16W/LED/ | 2 |  |  | 1L016 | 16 | 0 | 3200 | 0.032 | 102.4 | 0% | 0% | 0 | 102.4 | 16.9984 | 110.4896
55 | SITE LIGHTING FLAG | OUT | GRND/70W/MH/SEALED | 1M0070S | 2 | 95 | 0.19 | 3200 | 608 | 100.928 | NA | 0 |  |  | NA | 95 | 0 | 3200 | 0.19 | 608 | 0% | 0% | 0 | 608 | 100.928 | 0
[5 empty] | 512 |  | 47.41 |  | 151733.44 | 25187.751 |  | 417 | [6 empty] | 24.753 | 77055.76 |  |  |  | 77388.56 | 12846.501 | 12341.2501
Fixture Legend
| Annual Savings: |  | 12341.2501 | [6 empty] | ECM Qty | Measure ID | Description |  |  |  |  | Color | Lumens | Manufacturer |  | Part Number
| kW Reduced: |  | 22.657 | [6 empty] | 21 | KIT/DRUM_12W/LED | LED Drum Retrofit kit |  |  |  |  | 30-35K | 1500 | RemPhos |  | RPT-LEDCR-1600LM-3000K
| kWh Savings: |  | 74344.88 | [6 empty] | 16 | KIT/DRUM_18W/LED | LED Drum Retrofit kit |  |  |  |  | 35K | 2100 | RemPhos |  | RPT-LEDCR-2200LM-3000K
[10 empty] | 16 | KIT/POST_TOP/LED/60W/ | LED Retrofit kit, custom cut LED panel [1] |  |  |  |  | 5K | 5066 | LED Conversions |  | Retro-HTS-9R
[10 empty] | 2 | KIT/SCREW-IN_16W/LED/ | LED Retrofit, Screw-in |  |  |  |  | 4K | 1700 | RemPhos |  | RPT-LEDSS-1700LM-4000K-E26
[10 empty] | 236 | NEW/13W/LED/RECESSED CAN | New LED 6" Recessed Can |  |  |  |  | 35K | 900 | Sylvania |  | LED/RT5/6/HO//900/835
[10 empty] | 16 | NEW/LED/130W/SEN/STEP-DIM | New LED High Bay with integrated sensor |  |  |  |  | 4K | 18091 | Flex Lusio Essentials |  | ES3P-A-6MS-40-WIDE-FR-LV-CRM-10V-OCC40-CORDN-EMBN-OPTN
[10 empty] | 8 | NEW/LED/POST-TOP/45W | New LED Post Top for Rnd Pole |  |  |  |  | 5K | 5684 | Lithonia Lighting |  | DSX0 LED 20C 700 50K T3M MVOLT RPA DBLXD
[10 empty] | 70 | NEW/TT/LED/20W/ | New LED 2x2 troffer |  |  |  |  | 35K | 2213 | Lithonia Lighting |  | 2FSL2 20L EZ1 LP835
[10 empty] | 25 | RB/TT/22W_2BAR/_KIT | 2x2 Troffer, 2 Bar LED Retrofit kit |  |  |  |  | 35K | 2300 | Litetronics |  | RF-22-U-Q-T2-35
[10 empty] | 7 | RL/50W/LED/SCREW-IN | LED Retrofit, Screw-in |  |  |  |  | 4K | 4000 | RemPhos |  | RPT-LEDSSG2-5600LM-4000K-E39
[1] The custom cut is an in-field trimming to ensure that the retrofit kit fits well.

## Ripley
Concord School system - Ripley
Lighting Worksheet
Auditor: Barney Judge
| SITE LOCATION | Flr | EXISTING | PRODUCT | QTY | E-Watts | Total | RUN | kWh | ANNUAL COST | PROPOSED | QTY | Sensor | QTY | DEVICE | P-watts | StepDim | Prop | TOT | kWh | % Sen | % Power | KWH | Total | ANNUAL COST | Annual
Sort |  |  |  | CODE |  |  | KW | HRS | Pre | 0.164 |  |  | Type |  | CODE |  | 50%/Watts | RunHRS | KW | Post | saving | StepDim | SvDim | Post-KWH | (PROPOSED) | CostSving
| SITE LOCATION |  |  | E-Code | [6 empty] | PROPOSED | QTY |  |  | P-code
1 | CLASSROOM E1 | E | TF2F34/ESM | 2F40SEM | 13 | 70 | 0.91 | 3200 | 2912 | 477.568 | RB/TF/32W_2BAR/_KIT | 13 |  |  | 1L032 | 32 | 0 | 3200 | 0.416 | 1331.2 | 0% | 0% | 0 | 1331.2 | 218.3168 | 259.2512
2 | HALL | E | TF2F34/ESM | 2F40SEM | 2 | 70 | 0.14 | 3200 | 448 | 73.472 | RB/TF/32W_2BAR/_KIT | 2 |  |  | 1L032 | 32 | 0 | 3200 | 0.064 | 204.8 | 0% | 0% | 0 | 204.8 | 33.5872 | 39.8848
3 | BOYS ROOM | E | TF/3F32/E | 3F32SSE | 1 | 88 | 0.088 | 3200 | 281.6 | 46.1824 | RB/TF/50W_3BAR/_KIT | 1 |  |  | 1L050 | 50 | 0 | 3200 | 0.05 | 160 | 0% | 0% | 0 | 160 | 26.24 | 19.9424
4 | GIRLS ROOM | E | TF/3F32/E | 3F32SSE | 1 | 88 | 0.088 | 3200 | 281.6 | 46.1824 | RB/TF/50W_3BAR/_KIT | 1 |  |  | 1L050 | 50 | 0 | 3200 | 0.05 | 160 | 0% | 0% | 0 | 160 | 26.24 | 19.9424
5 | CLASSROOM E2 | E | TF/4F34/ESM | 4F40SEM | 7 | 140 | 0.98 | 3200 | 3136 | 514.304 | RB/TF/50W_3BAR/_KIT | 7 |  |  | 1L050 | 50 | 0 | 3200 | 0.35 | 1120 | 0% | 0% | 0 | 1120 | 183.68 | 330.624
6 | MRS SUMMERS OFC | E | TF/4F34/ESM | 4F40SEM | 2 | 140 | 0.28 | 3200 | 896 | 146.944 | RB/TF/50W_3BAR/_KIT | 2 |  |  | 1L050 | 50 | 0 | 3200 | 0.1 | 320 | 0% | 0% | 0 | 320 | 52.48 | 94.464
7 | NEXT OFFICE | E | TF/4F34/ESM | 4F40SEM | 2 | 140 | 0.28 | 3200 | 896 | 146.944 | RB/TF/50W_3BAR/_KIT | 2 |  |  | 1L050 | 50 | 0 | 3200 | 0.1 | 320 | 0% | 0% | 0 | 320 | 52.48 | 94.464
8 | OFFICE | E | TF/4F34/ESM | 4F40SEM | 2 | 140 | 0.28 | 3200 | 896 | 146.944 | RB/TF/50W_3BAR/_KIT | 2 |  |  | 1L050 | 50 | 0 | 3200 | 0.1 | 320 | 0% | 0% | 0 | 320 | 52.48 | 94.464
9 | OFFICE | E | TF/4F34/ESM | 4F40SEM | 2 | 140 | 0.28 | 3200 | 896 | 146.944 | RB/TF/50W_3BAR/_KIT | 2 |  |  | 1L050 | 50 | 0 | 3200 | 0.1 | 320 | 0% | 0% | 0 | 320 | 52.48 | 94.464
10 | CLASSROOM A1 | A | TF/3F32/E | 3F32SSE | 11 | 88 | 0.968 | 2000 | 1936 | 317.504 | RB/TF/50W_3BAR/_KIT | 11 |  |  | 1L050 | 50 | 0 | 2000 | 0.55 | 1100 | 0% | 0% | 0 | 1100 | 180.4 | 137.104
11 | BOYS ROOM | A | TF/3F32/E | 3F32SSE | 1 | 88 | 0.088 | 2000 | 176 | 28.864 | RB/TF/50W_3BAR/_KIT | 1 |  |  | 1L050 | 50 | 0 | 2000 | 0.05 | 100 | 0% | 0% | 0 | 100 | 16.4 | 12.464
12 | GIRLS ROOM | A | TF/3F32/E | 3F32SSE | 1 | 88 | 0.088 | 2000 | 176 | 28.864 | RB/TF/50W_3BAR/_KIT | 1 |  |  | 1L050 | 50 | 0 | 2000 | 0.05 | 100 | 0% | 0% | 0 | 100 | 16.4 | 12.464
13 | CLASSROOM A2 | A | TF/3F32/E | 3F32SSE | 11 | 88 | 0.968 | 2000 | 1936 | 317.504 | RB/TF/50W_3BAR/_KIT | 11 |  |  | 1L050 | 50 | 0 | 2000 | 0.55 | 1100 | 0% | 0% | 0 | 1100 | 180.4 | 137.104
14 | HALL | A | TF/3F32/E | 3F32SSE | 2 | 88 | 0.176 | 2000 | 352 | 57.728 | RB/TF/50W_3BAR/_KIT | 2 |  |  | 1L050 | 50 | 0 | 2000 | 0.1 | 200 | 0% | 0% | 0 | 200 | 32.8 | 24.928
15 | CLASSROOM C1 | C | TF/3F32/E | 3F32SSE | 11 | 88 | 0.968 | 3200 | 3097.6 | 508.0064 | RB/TF/50W_3BAR/_KIT | 11 |  |  | 1L050 | 50 | 0 | 3200 | 0.55 | 1760 | 0% | 0% | 0 | 1760 | 288.64 | 219.3664
16 | CLASSROOM C2 | C | TF/3F32/E | 3F32SSE | 10 | 88 | 0.88 | 3200 | 2816 | 461.824 | RB/TF/50W_3BAR/_KIT | 10 |  |  | 1L050 | 50 | 0 | 3200 | 0.5 | 1600 | 0% | 0% | 0 | 1600 | 262.4 | 199.424
17 | BOYS ROOM | C | TF/3F32/E | 3F32SSE | 1 | 88 | 0.088 | 3200 | 281.6 | 46.1824 | RB/TF/50W_3BAR/_KIT | 1 |  |  | 1L050 | 50 | 0 | 3200 | 0.05 | 160 | 0% | 0% | 0 | 160 | 26.24 | 19.9424
18 | GIRLS ROOM | C | TF/3F32/E | 3F32SSE | 1 | 88 | 0.088 | 3200 | 281.6 | 46.1824 | RB/TF/50W_3BAR/_KIT | 1 |  |  | 1L050 | 50 | 0 | 3200 | 0.05 | 160 | 0% | 0% | 0 | 160 | 26.24 | 19.9424
19 | HALL | C | TF/3F32/E | 3F32SSE | 2 | 88 | 0.176 | 3200 | 563.2 | 92.3648 | RB/TF/50W_3BAR/_KIT | 2 |  |  | 1L050 | 50 | 0 | 3200 | 0.1 | 320 | 0% | 0% | 0 | 320 | 52.48 | 39.8848
20 | CLASSROOM B1 | B | TF/3F32/E | 3F32SSE | 11 | 88 | 0.968 | 3200 | 3097.6 | 508.0064 | RB/TF/50W_3BAR/_KIT | 11 |  |  | 1L050 | 50 | 0 | 3200 | 0.55 | 1760 | 0% | 0% | 0 | 1760 | 288.64 | 219.3664
21 | CLASSROOM B2 | B | TF/3F32/E | 3F32SSE | 11 | 88 | 0.968 | 3200 | 3097.6 | 508.0064 | RB/TF/50W_3BAR/_KIT | 11 |  |  | 1L050 | 50 | 0 | 3200 | 0.55 | 1760 | 0% | 0% | 0 | 1760 | 288.64 | 219.3664
22 | BOYS ROOM | B | TF/3F32/E | 3F32SSE | 1 | 88 | 0.088 | 3200 | 281.6 | 46.1824 | RB/TF/50W_3BAR/_KIT | 1 |  |  | 1L050 | 50 | 0 | 3200 | 0.05 | 160 | 0% | 0% | 0 | 160 | 26.24 | 19.9424
23 | GIRLS ROOM | B | TF/3F32/E | 3F32SSE | 1 | 88 | 0.088 | 3200 | 281.6 | 46.1824 | RB/TF/50W_3BAR/_KIT | 1 |  |  | 1L050 | 50 | 0 | 3200 | 0.05 | 160 | 0% | 0% | 0 | 160 | 26.24 | 19.9424
24 | HALL | B | TF/3F32/E | 3F32SSE | 2 | 88 | 0.176 | 3200 | 563.2 | 92.3648 | RB/TF/50W_3BAR/_KIT | 2 |  |  | 1L050 | 50 | 0 | 3200 | 0.1 | 320 | 0% | 0% | 0 | 320 | 52.48 | 39.8848
25 | OFFICE | D | W4/2F32/E | 2F32SSE | 4 | 60 | 0.24 | 3200 | 768 | 125.952 | RB/2L-4'/LED/TUBE/32W_ | 4 |  |  | 1L032 | 32 | 0 | 3200 | 0.128 | 409.6 | 0% | 0% | 0 | 409.6 | 67.1744 | 58.7776
26 | RESTROOM | D | VN2/1F20/S | 1F20SSS | 1 | 32 | 0.032 | 3200 | 102.4 | 16.7936 | RB/1L-2'/LED/TUBE/9W_ | 1 |  |  | 1L013 | 13 | 0 | 3200 | 0.013 | 41.6 | 0% | 0% | 0 | 41.6 | 6.8224 | 9.9712
27 | RESTROOM | D | VN2/1F20/S | 1F20SSS | 1 | 32 | 0.032 | 3200 | 102.4 | 16.7936 | RB/1L-2'/LED/TUBE/9W_ | 1 |  |  | 1L013 | 13 | 0 | 3200 | 0.013 | 41.6 | 0% | 0% | 0 | 41.6 | 6.8224 | 9.9712
28 | CONF ROOM | D | TF/3F32/E | 3F32SSE | 6 | 88 | 0.528 | 3200 | 1689.6 | 277.0944 | RB/TF/50W_3BAR/_KIT | 6 |  |  | 1L050 | 50 | 0 | 3200 | 0.3 | 960 | 0% | 0% | 0 | 960 | 157.44 | 119.6544
29 | CLASSROOM 1 | D | TF/4F32/E | 4F32SSE | 4 | 112 | 0.448 | 3200 | 1433.6 | 235.1104 | RB/TF/50W_3BAR/_KIT | 4 |  |  | 1L050 | 50 | 0 | 3200 | 0.2 | 640 | 0% | 0% | 0 | 640 | 104.96 | 130.1504
30 | CLASSROOM 2 | D | TF/4F32/E | 4F32SSE | 2 | 112 | 0.224 | 3200 | 716.8 | 117.5552 | RB/TF/50W_3BAR/_KIT | 2 |  |  | 1L050 | 50 | 0 | 3200 | 0.1 | 320 | 0% | 0% | 0 | 320 | 52.48 | 65.0752
31 | PARENT/CHILD PROG OFC | D | TF/3F32/E | 3F32SSE | 6 | 88 | 0.528 | 2000 | 1056 | 173.184 | RB/TF/50W_3BAR/_KIT | 6 |  |  | 1L050 | 50 | 0 | 2000 | 0.3 | 600 | 0% | 0% | 0 | 600 | 98.4 | 74.784
32 | RESTROOM | D | TF/3F32/E | 3F32SSE | 1 | 88 | 0.088 | 2000 | 176 | 28.864 | RB/TF/50W_3BAR/_KIT | 1 |  |  | 1L050 | 50 | 0 | 2000 | 0.05 | 100 | 0% | 0% | 0 | 100 | 16.4 | 12.464
33 | JANITOR | D | 130W/INC/KEYLESS | 1I0100 | 1 | 100 | 0.1 | 1000 | 100 | 16.4 | RL/A19-LED/17W/SCREW-IN | 1 |  |  | 1L017 | 17 | 0 | 1000 | 0.017 | 17 | 0% | 0% | 0 | 17 | 2.788 | 13.612
34 | HALLWAY/WINDOWS | D | W4/2F34/ESM | 2F40SEM | 18 | 70 | 1.26 | 3200 | 4032 | 661.248 | RB/2L-4'/LED/TUBE/32W_ | 18 |  |  | 1L032 | 32 | 0 | 3200 | 0.576 | 1843.2 | 0% | 0% | 0 | 1843.2 | 302.2848 | 358.9632
35 | HALL TO BOILER ROOM | 1 | W4/2F32/E | 2F32SSE | 2 | 60 | 0.12 | 3200 | 384 | 62.976 | RB/2L-4'/LED/TUBE/32W_ | 2 |  |  | 1L032 | 32 | 0 | 3200 | 0.064 | 204.8 | 0% | 0% | 0 | 204.8 | 33.5872 | 29.3888
36 | STORAGE CURRICULUM | 1 | EGGCREATE/W8/2F96/S | 2F96SSS | 1 | 173 | 0.173 | 3200 | 553.6 | 90.7904 | NEW/8'_STRIP/LED/60W | 1 |  |  | 1L064 | 60 | 0 | 3200 | 0.06 | 192 | 0% | 0% | 0 | 192 | 31.488 | 59.3024
37 | OLD KITCHEN | 1 | W4/2F32/E | 2F32SSE | 1 | 60 | 0.06 | 3200 | 192 | 31.488 | RB/2L-4'/LED/TUBE/32W_ | 1 |  |  | 1L032 | 32 | 0 | 3200 | 0.032 | 102.4 | 0% | 0% | 0 | 102.4 | 16.7936 | 14.6944
38 | JANITOR | 1 | 100W/INC/KEYLESS | 1I0100 | 1 | 100 | 0.1 | 3200 | 320 | 52.48 | RL/A19-LED/17W/SCREW-IN | 1 |  |  | 1L017 | 17 | 0 | 3200 | 0.017 | 54.4 | 0% | 0% | 0 | 54.4 | 8.9216 | 43.5584
39 | MAINTENANCE TO CLASSRM | 1 | IH8/2F96/ESM | 2F96SEM | 11 | 123 | 1.353 | 3200 | 4329.6 | 710.0544 | NEW/8'_STRIP/LED/60W | 11 |  |  | 1L064 | 60 | 0 | 3200 | 0.66 | 2112 | 0% | 0% | 0 | 2112 | 346.368 | 363.6864
40 | JANITOR/HVAC | 1 | 52W/INC/KEYLESS | 1I0052 | 1 | 52 | 0.052 | 3200 | 166.4 | 27.2896 | RL/A19-LED/17W/SCREW-IN | 1 |  |  | 1L017 | 17 | 0 | 3200 | 0.017 | 54.4 | 0% | 0% | 0 | 54.4 | 8.9216 | 18.368
41 | STORAGE | 1 | S8/2F34/STD | 2F40SSM | 6 | 86 | 0.516 | 3200 | 1651.2 | 270.7968 | RB/2L-4'/LED/TUBE/32W_ | 6 |  |  | 1L032 | 32 | 0 | 3200 | 0.192 | 614.4 | 0% | 0% | 0 | 614.4 | 100.7616 | 170.0352
42 | STORAGE | 1 | S4/1F40/STD | 1F40SSS | 1 | 57 | 0.057 | 3200 | 182.4 | 29.9136 | RB/1L-4'/LED/TUBE/16W_ | 1 |  |  | 1L016 | 16 | 0 | 3200 | 0.016 | 51.2 | 0% | 0% | 0 | 51.2 | 8.3968 | 21.5168
43 | CONF ROOM 1 | 1 | TF/4F34/ESM | 4F40SEM | 8 | 140 | 1.12 | 3200 | 3584 | 587.776 | RB/TF/50W_3BAR/_KIT | 8 |  |  | 1L050 | 50 | 0 | 3200 | 0.4 | 1280 | 0% | 0% | 0 | 1280 | 209.92 | 377.856
44 | STORAGE | 1 | W4/2F40/STD | 2F40SSS | 3 | 94 | 0.282 | 3200 | 902.4 | 147.9936 | RB/2L-4'/LED/TUBE/32W_ | 3 |  |  | 1L032 | 32 | 0 | 3200 | 0.096 | 307.2 | 0% | 0% | 0 | 307.2 | 50.3808 | 97.6128
45 | GYM CLOSET | 1 | CHINA HAT/65W/PAR30 | 1I0065 | 1 | 65 | 0.065 | 3200 | 208 | 34.112 | RL/A19-LED/17W/SCREW-IN | 1 |  |  | 1L017 | 17 | 0 | 3200 | 0.017 | 54.4 | 0% | 0% | 0 | 54.4 | 8.9216 | 25.1904
46 | RESTROOM | 1 | VN4/1F32/E | 1F32SSE | 1 | 30 | 0.03 | 3200 | 96 | 15.744 | RB/1L-4'/LED/TUBE/16W_ | 1 |  |  | 1L016 | 16 | 0 | 3200 | 0.016 | 51.2 | 0% | 0% | 0 | 51.2 | 8.3968 | 7.3472
47 | RESTROOM | 1 | O4/2F32/E | 2F32SSE | 1 | 60 | 0.06 | 3200 | 192 | 31.488 | RB/2L-4'/LED/TUBE/32W_ | 1 |  |  | 1L032 | 32 | 0 | 3200 | 0.032 | 102.4 | 0% | 0% | 0 | 102.4 | 16.7936 | 14.6944
48 | OLD REST ROOM | 1 | O4/2F34/STD | 2F40SSM | 1 | 86 | 0.086 | 3200 | 275.2 | 45.1328 | RB/2L-4'/LED/TUBE/32W_ | 1 |  |  | 1L032 | 32 | 0 | 3200 | 0.032 | 102.4 | 0% | 0% | 0 | 102.4 | 16.7936 | 28.3392
49 | STORAGE | 1 | VN4/1F34/STD | 1F40SSM | 1 | 50 | 0.05 | 3200 | 160 | 26.24 | RB/1L-4'/LED/TUBE/16W_ | 1 |  |  | 1L016 | 16 | 0 | 3200 | 0.016 | 51.2 | 0% | 0% | 0 | 51.2 | 8.3968 | 17.8432
50 | COMP STORAGE WORK RM | 1 | TF/4F34/ESM | 4F40SEM | 12 | 140 | 1.68 | 3200 | 5376 | 881.664 | RB/TF/50W_3BAR/_KIT | 12 |  |  | 1L050 | 50 | 0 | 3200 | 0.6 | 1920 | 0% | 0% | 0 | 1920 | 314.88 | 566.784
51 | WORK RM STORAGE | 1 | TF/4F34/ESM | 4F40SEM | 2 | 140 | 0.28 | 3200 | 896 | 146.944 | RB/TF/50W_3BAR/_KIT | 2 |  |  | 1L050 | 50 | 0 | 3200 | 0.1 | 320 | 0% | 0% | 0 | 320 | 52.48 | 94.464
52 | MAIN HALLWAY | 1 | W4/2F34/ESM | 2F40SEM | 9 | 70 | 0.63 | 3200 | 2016 | 330.624 | RB/2L-4'/LED/TUBE/32W_ | 9 |  |  | 1L032 | 32 | 0 | 3200 | 0.288 | 921.6 | 0% | 0% | 0 | 921.6 | 151.1424 | 179.4816
53 | OFC-NUT | 1 | TF/3F32/E | 3F32SSE | 2 | 88 | 0.176 | 3200 | 563.2 | 92.3648 | RB/TF/50W_3BAR/_KIT | 2 |  |  | 1L050 | 50 | 0 | 3200 | 0.1 | 320 | 0% | 0% | 0 | 320 | 52.48 | 39.8848
54 | CLOSET/FILE STORAGE | 1 | TF/4F34/ESM | 4F40SEM | 2 | 140 | 0.28 | 3200 | 896 | 146.944 | RB/TF/50W_3BAR/_KIT | 2 |  |  | 1L050 | 50 | 0 | 3200 | 0.1 | 320 | 0% | 0% | 0 | 320 | 52.48 | 94.464
55 | COPY CENTER | 1 | S8/2F96/ESM | 2F96SEM | 8 | 123 | 0.984 | 3200 | 3148.8 | 516.4032 | RB-KIT/4L-4'/LED/TUBE/64W_ | 8 |  |  | 1L064 | 64 | 0 | 3200 | 0.512 | 1638.4 | 0% | 0% | 0 | 1638.4 | 268.6976 | 247.7056
56 | HALLWAY | 1 | W4/2F34/ESM | 2F40SEM | 10 | 70 | 0.7 | 3200 | 2240 | 367.36 | RB/2L-4'/LED/TUBE/32W_ | 10 |  |  | 1L032 | 32 | 0 | 3200 | 0.32 | 1024 | 0% | 0% | 0 | 1024 | 167.936 | 199.424
57 | WOMENS RM 1 | 1 | O4/2F32/E | 2F32SSE | 1 | 60 | 0.06 | 3200 | 192 | 31.488 | RB/2L-4'/LED/TUBE/32W_ | 1 |  |  | 1L032 | 32 | 0 | 3200 | 0.032 | 102.4 | 0% | 0% | 0 | 102.4 | 16.7936 | 14.6944
58 | WOMENS RM 1 | 1 | VN4/2F32/E | 2F32SSE | 1 | 60 | 0.06 | 3200 | 192 | 31.488 | RB/2L-4'/LED/TUBE/32W_ | 1 |  |  | 1L032 | 32 | 0 | 3200 | 0.032 | 102.4 | 0% | 0% | 0 | 102.4 | 16.7936 | 14.6944
59 | WOMENS RM 2 | 1 | O4/2F32/E | 2F32SSE | 1 | 60 | 0.06 | 3200 | 192 | 31.488 | RB/2L-4'/LED/TUBE/32W_ | 1 |  |  | 1L032 | 32 | 0 | 3200 | 0.032 | 102.4 | 0% | 0% | 0 | 102.4 | 16.7936 | 14.6944
60 | WOMENS RM 2 | 1 | VN2/2F17/E | 2F17SSE | 3 | 37 | 0.111 | 3200 | 355.2 | 58.2528 | RB/2L-2'/LED/TUBE/18W | 3 |  |  | 1L026 | 26 | 0 | 3200 | 0.078 | 249.6 | 0% | 0% | 0 | 249.6 | 40.9344 | 17.3184
61 | CPT LENDING ROOM | 1 | EGGCREATE/IH8/2F96/S | 2F96SEM | 1 | 123 | 0.123 | 3200 | 393.6 | 64.5504 | NEW/8'_STRIP/LED/60W | 1 |  |  | 1L064 | 60 | 0 | 3200 | 0.06 | 192 | 0% | 0% | 0 | 192 | 31.488 | 33.0624
62 | MENS | 1 | O4/2F32/E | 2F32SSE | 2 | 60 | 0.12 | 3200 | 384 | 62.976 | RB/2L-4'/LED/TUBE/32W_ | 2 |  |  | 1L032 | 32 | 0 | 3200 | 0.064 | 204.8 | 0% | 0% | 0 | 204.8 | 33.5872 | 29.3888
63 | MENS | 1 | VN2/2F17/E | 2F17SSE | 2 | 37 | 0.074 | 3200 | 236.8 | 38.8352 | RB/2L-2'/LED/TUBE/18W | 2 |  |  | 1L026 | 18 | 0 | 3200 | 0.036 | 115.2 | 0% | 0% | 0 | 115.2 | 18.8928 | 19.9424
64 | SITE LIGHTING | OUT | WP/100W/MH | 1M0100S | 2 | 120 | 0.24 | 4380 | 768 | 125.952 | NEW/39W/-WALLPACK/PC | 2 |  |  | 1L039 | 39 | 0 | 4380 | 0.078 | 341.64 | 0% | 0% | 0 | 341.64 | 56.029 | 69.923
65 | SITE LIGHTING | OUT | WP/175W/MH | 1M0175S | 5 | 205 | 1.025 | 4380 | 4489.5 | 736.278 | NEW/39W/WALLPACK/PC | 5 |  |  | 1L039 | 39 | 0 | 4380 | 0.195 | 854.1 | 0% | 0% | 0 | 854.1 | 140.0724 | 596.2056
66 | SITE LIGHTING | OUT | FLD/100W/MH | 1M0100S | 2 | 120 | 0.24 | 4380 | 1051.2 | 172.3968 | NEW/LED/FLD/27W/PC | 2 |  |  | 1L027 | 27 | 0 | 4380 | 0.054 | 236.52 | 0% | 0% | 0 | 236.52 | 38.7893 | 133.6075
67 | SITE LIGHTING | OUT | RC/90W/PAR38 | 1I0090 | 3 | 90 | 0.27 | 4380 | 1182.6 | 193.9464 | RL/LED/16W/PAR38 | 3 |  |  | 1L016 | 16 | 0 | 4380 | 0.048 | 210.24 | 0% | 0% | 0 | 210.24 | 34.4794 | 159.467
68 | SITE LIGHTING | OUT | DRUM/42W/CFL | 1C0042E | 8 | 48 | 0.384 | 4380 | 1681.92 | 275.8349 | KIT/DRUM_12W/LED/ | 8 |  |  | 1L012 | 12 | 0 | 4380 | 0.096 | 420.48 | 0% | 0% | 0 | 420.48 | 68.9587 | 206.8762
69 | SITE LIGHTING | OUT | WP/150W/MH | 1M0150S | 3 | 190 | 0.57 | 4380 | 2496.6 | 409.4424 | NEW/57W/WALLPACK/PC | 3 |  |  | 1L039 | 57 | 0 | 4380 | 0.171 | 748.98 | 0% | 0% | 0 | 748.98 | 122.8327 | 286.6097
70 | SITE LIGHTING | OUT | W4/1F34/ESM | 1F40SEM | 11 | 40 | 0.44 | 4380 | 1927.2 | 316.0608 | RB/1L-4'/LED/TUBE/16W_ | 11 |  |  | 1L016 | 16 | 0 | 4380 | 0.176 | 770.88 | 0% | 0% | 0 | 770.88 | 126.4243 | 189.6365
71 | SITE LIGHTING FLAG POLE | OUT | INGROUND/70W/MH/SEALED | 1M0070S | 2 | 95 | 0.19 | 4380 | 832.2 | 136.4808 | NA | 0 |  |  | NA | 95 | 0 | 4380 | 0.19 | 832.2 | 0% | 0% | 0 | 832.2 | 136.4808 | 0
[5 empty] | 285 |  | 26.403 |  | 84465.22 | 13852.2961 |  | 283 | [6 empty] | 11.906 | 37271.24 |  |  |  | 37271.24 | 6112.4834 | 7739.8127
Fixture Legend
| Annual Savings: |  | 7739.8127 | [6 empty] | ECM Qty | Measure ID | Description |  |  |  |  | Color | Lumens | Manufacturer |  | Part Number
| kW Reduced: |  | 14.497 | [6 empty] | 8 | KIT/DRUM_12W/LED/ | LED Drum Retrofit kit |  |  |  |  | 30-35K | 1500 | RemPhos |  | RPT-LEDCR-1600LM-3000K
| kWh Savings: |  | 47193.98 | [6 empty] | 10 | NEW/57W/WALLPACK/PC | New LED wall pack with PC |  |  |  |  | 5K | 4312 | RAB Lighting |  | SLIM-57/PC
[10 empty] | 13 | NEW/8'_STRIP/LED/60W | New LED 8' strip fixture |  |  |  |  | 35K | 7144 | Lithonia |  | TZL1N L96 6000LM FST MVOLT 35K 80CRI WH
[10 empty] | 2 | NEW/LED/FLD/27W/PC | New LED Flood with PC |  |  |  |  | 5K | 2901 | RAB Lighting |  | FFLED26/PC
[10 empty] | 2 | RB/1L-2'/LED/TUBE/9W_ | Relamp w/ TLED's and new Electronic Ballast |  |  |  |  | 35K | 1150 | Universal EverLine |  | T8LDR2F9/835A; - Universal Triad B132IUNVEL-N
[10 empty] | 14 | RB/1L-4'/LED/TUBE/16W_ | Relamp w/ TLED's and new Electronic Ballast |  |  |  |  | 35K | 2200 | Universal EverLine |  | T8LDR4F15/835A - Universal Triad B132IUNVELHE-N
[10 empty] | 5 | RB/2L-2'/LED/TUBE/18W_ | Relamp w/ TLED's and new Electronic Ballast |  |  |  |  | 35K | 2300 | Universal EverLine |  | T8LDR2F9/835A; - Universal Triad B232IUNVELHE-N
[10 empty] | 60 | RB/2L-4'/LED/TUBE/32W_ | Relamp w/ TLED's and new Electronic Ballast |  |  |  |  | 35K | 4400 | Universal EverLine |  | T8LDR4F15/835A - Universal Triad B232IUNVELHE-N
[10 empty] | 15 | RB/TF/32W_2BAR/_KIT | 2x4 Troffer, 2 Bar LED Retrofit kit |  |  |  |  | 35K | 3600 | Litetronics |  | RF-32-U-Q-T4-35
[10 empty] | 139 | RB/TF/50W_3BAR/_KIT | 2x4 Troffer, 3 Bar LED Retrofit kit |  |  |  |  | 35K | 5850 | Litetronics |  | RF-50-U-Q-T4-35
[10 empty] | 8 | RB-KIT/4L-4'/LED/TUBE/64W_ | Strip Kit w/ TLED's and new Electronic Ballast |  |  |  |  | 35K | 8800 | Universal EverLine |  | T8LDR4F15/835A / Universal Triad B432IUNVELHE-N / Renova Strip Kit | [5 empty] | 1x8 Strip Retro Kit - 4 Lamp T8 - Unv Brkt - White Ballast Cover - | SRK-18-B-4LT8-UNV5.8-B(IS)
[10 empty] | 4 | RL/A19-LED/15W/SCREW-IN | New Screw-in A19 LED |  |  |  |  | 27K | 1600 | Sylvania |  | LED15A21/DIM/O/827/G4
[10 empty] | 3 | RL/LED/16W/PAR38 | New Screw-in PAR38 LED |  |  |  |  | 27K | 1000 | Sylvania |  | LED16PAR38/DIM/827/NFL25/G3

## Alcott
Concord School system - Alcott
Lighting Worksheet
Auditor: Barney Judge
| SITE LOCATION | Flr | EXISTING | PRODUCT | QTY | E-Watts | Total | RUN | kWh | ANNUAL COST | PROPOSED | QTY | Sensor | QTY | DEVICE | P-watts | StepDim | Prop | TOT | kWh | % Sen | % Power | KWH | Total | ANNUAL COST | Annual | Color | Total | Payback | Cost Net of Rebate
Sort |  |  |  | CODE |  |  | KW | HRS | Pre | 0.174 |  |  | Type |  | CODE |  | 50%/Watts | RunHRS | KW | Post | saving | StepDim | SvDim | Post-KWH | (PROPOSED) | CostSving | Temp | ECM Cost | Period
| SITE LOCATION |  |  | E-Code | [6 empty] | PROPOSED | QTY |  |  | P-code
1 | LOBBY A129 | 1 | TT/2FB31/E/9-CELL | 2F32SSE | 8 | 60 | 0.48 | 3200 | 1536 | 267.264 | RB/TT/22W_2BAR/_KIT | 8 |  |  | 1L020 | 22 | 0 | 3200 | 0.176 | 563.2 | 0% | 0% | 0 | 563.2 | 97.9968 | 169.2672 | 35K | 1614.0103 | 9.5353 | 1310.0103
2 | FACULTY A132 | 1 | TT/2FB31/E | 2F32SSE | 1 | 60 | 0.06 | 3200 | 192 | 33.408 | RB/TT/22W_2BAR/_KIT | 1 |  |  | 1L020 | 22 | 0 | 3200 | 0.022 | 70.4 | 0% | 0% | 0 | 70.4 | 12.2496 | 21.1584 | 35K | 201.7513 | 9.5353 | 163.7513
3 | MENS A135 | 1 | RC6/2X18W/CFL | 2C0018E | 3 | 40 | 0.12 | 3200 | 384 | 66.816 | NEW/13W/LED/RECESSED CAN | 3 |  |  | 1L013 | 13 | 0 | 3200 | 0.039 | 124.8 | 0% | 0% | 0 | 124.8 | 21.7152 | 45.1008 | 35K | 701.1859 | 15.5471 | 620.1859
4 | WOMENS A136 | 1 | RC6/2X18W/CFL | 2C0018E | 3 | 40 | 0.12 | 3200 | 384 | 66.816 | NEW/13W/LED/RECESSED CAN | 3 |  |  | 1L013 | 13 | 0 | 3200 | 0.039 | 124.8 | 0% | 0% | 0 | 124.8 | 21.7152 | 45.1008 | 35K | 701.1859 | 15.5471 | 620.1859
5 | HALL | 1 | RC6/2X18W/CFL | 2C0018E | 1 | 40 | 0.04 | 3200 | 128 | 22.272 | NEW/13W/LED/RECESSED CAN | 1 |  |  | 1L013 | 13 | 0 | 3200 | 0.013 | 41.6 | 0% | 0% | 0 | 41.6 | 7.2384 | 15.0336 | 35K | 233.7286 | 15.5471 | 206.7286
6 | GYM A121 | 1 | HIGHBAY/250W/MH | 1M0250S | 12 | 295 | 3.54 | 3200 | 11328 | 1971.072 | NEW/LED/86W/SEN/STEP-DIM | 12 | integrated | 12 | 1L088 | 86 | 17.2 | 2400 | 1.032 | 2476.8 | 25% | 0% | 165.12 | 2641.92 | 459.6941 | 1511.3779 | 4K | 11004.1301 | 7.2809 | 8496.1301
7 | GYM A121 | 1 | RC6/2X18W/CFL | 2C0018E | 2 | 40 | 0.08 | 3200 | 256 | 44.544 | NEW/13W/LED/RECESSED CAN | 2 |  |  | 1L013 | 13 | 0 | 3200 | 0.026 | 83.2 | 0% | 0% | 0 | 83.2 | 14.4768 | 30.0672 | 35K | 467.4573 | 15.5471 | 413.4573
8 | RESTROOM A123 | 1 | RC6/2X18W/CFL | 2C0018E | 2 | 40 | 0.08 | 3200 | 256 | 44.544 | NEW/13W/LED/RECESSED CAN | 2 |  |  | 1L013 | 13 | 0 | 3200 | 0.026 | 83.2 | 0% | 0% | 0 | 83.2 | 14.4768 | 30.0672 | 35K | 467.4573 | 15.5471 | 413.4573
9 | DOOR 24 ENTRANCE | 1 | TT/2FB31/E/9-CELL | 2F32SSE | 1 | 60 | 0.06 | 3200 | 192 | 33.408 | RB/TT/22W_2BAR/_KIT | 1 |  |  | 1L020 | 22 | 0 | 3200 | 0.022 | 70.4 | 0% | 0% | 0 | 70.4 | 12.2496 | 21.1584 | 35K | 201.7513 | 9.5353 | 163.7513
10 | AUDITORIUM A129 | 1 | 18"/DRUM/38W/FLOUR | 0 | 16 | 40 | 0.64 | 2000 | 1280 | 222.72 | KIT/DRUM_12W/LED/ | 16 |  |  | 1L012 | 12 | 0 | 2000 | 0.192 | 384 | 0% | 0% | 0 | 384 | 66.816 | 155.904 | 35K | 3513.0556 | 22.5335 | 3065.0556
11 | AUDITORIUM A129 | 1 | RC12/250W/MH | 1M0250S | 2 | 295 | 0.59 | 2000 | 1180 | 205.32 | NA | 0 |  |  | NA | 295 | 0 | 2000 | 0.59 | 1180 | 0% | 0% | 0 | 1180 | 205.32 | 0 | 35K | 0 |  | 0
12 | AUDITORIUM A129 | 1 | PEND/CYLINDER/250W/MH | 1M0250S | 6 | 295 | 1.77 | 2000 | 3540 | 615.96 | NA | 0 |  |  | NA | 295 | 0 | 2000 | 1.77 | 3540 | 0% | 0% | 0 | 3540 | 615.96 | 0 | 35K | 0 |  | 0
13 | AUDITORIUM A129 | 1 | PEND/CYLINDER/100W/HALOGEN | 1T0100 | 18 | 100 | 1.8 | 2000 | 3600 | 626.4 | NA | 0 |  |  | NA | 100 | 0 | 2000 | 1.8 | 3600 | 0% | 0% | 0 | 3600 | 626.4 | 0 | 35K | 0 |  | 0
14 | AUDITORIUM A129 | 1 | RC10/100W/PAR38 | 1I0100 | 3 | 100 | 0.3 | 2000 | 600 | 104.4 | NA | 0 |  |  | NA | 100 | 0 | 2000 | 0.3 | 600 | 0% | 0% | 0 | 600 | 104.4 | 0 | 35K | 0 |  | 0
15 | DOOR 19 HALL | 1 | TT/2FB31/E/9-CELL | 2F32SSE | 1 | 60 | 0.06 | 3200 | 192 | 33.408 | RB/TT/22W_2BAR/_KIT | 1 |  |  | 1L020 | 22 | 0 | 3200 | 0.022 | 70.4 | 0% | 0% | 0 | 70.4 | 12.2496 | 21.1584 | 35K | 201.7513 | 9.5353 | 163.7513
16 | STAIRWELL DOOR 19 | 1 | 18"DRUM/28W/FLOUR | 0 | 2 | 30 | 0.06 | 3200 | 192 | 33.408 | KIT/DRUM_7W/LED/ | 2 |  |  | 1L007 | 7 | 0 | 3200 | 0.014 | 44.8 | 0% | 0% | 0 | 44.8 | 7.7952 | 25.6128 | 35K | 424.8802 | 16.5886 | 378.8802
17 | STAIRWELL DOOR 19 | 1 | TT/2FB31/E/9-CELL | 2F32SSE | 1 | 60 | 0.06 | 3200 | 192 | 33.408 | RB/TT/22W_2BAR/_KIT | 1 |  |  | 1L020 | 22 | 0 | 3200 | 0.022 | 70.4 | 0% | 0% | 0 | 70.4 | 12.2496 | 21.1584 | 35K | 201.7513 | 9.5353 | 163.7513
18 | BOYS ROOM A212 | 2 | RC6/2X18W/CFL | 2C0018E | 2 | 40 | 0.08 | 3200 | 256 | 44.544 | NEW/13W/LED/RECESSED CAN | 2 |  |  | 1L013 | 13 | 0 | 3200 | 0.026 | 83.2 | 0% | 0% | 0 | 83.2 | 14.4768 | 30.0672 | 35K | 467.4573 | 15.5471 | 413.4573
19 | GIRLS ROOM A213 | 2 | RC6/2X18W/CFL | 2C0018E | 2 | 40 | 0.08 | 3200 | 256 | 44.544 | NEW/13W/LED/RECESSED CAN | 2 |  |  | 1L013 | 13 | 0 | 3200 | 0.026 | 83.2 | 0% | 0% | 0 | 83.2 | 14.4768 | 30.0672 | 35K | 467.4573 | 15.5471 | 413.4573
20 | 1ST FLOOR HALL | 1 | RC6/2X18W/CFL | 2C0018E | 16 | 40 | 0.64 | 3200 | 2048 | 356.352 | NEW/13W/LED/RECESSED CAN | 16 |  |  | 1L013 | 13 | 0 | 3200 | 0.208 | 665.6 | 0% | 0% | 0 | 665.6 | 115.8144 | 240.5376 | 35K | 3739.6584 | 15.5471 | 3307.6584
21 | 1ST FLOOR HALL | 1 | RC6/2X18W/CFL | 2C0018E | 41 | 40 | 1.64 | 3200 | 5248 | 913.152 | NEW/13W/LED/RECESSED CAN | 41 |  |  | 1L013 | 13 | 0 | 3200 | 0.533 | 1705.6 | 0% | 0% | 0 | 1705.6 | 296.7744 | 616.3776 | 35K | 9582.8746 | 15.5471 | 8475.8746
22 | 2ND FLOOR HALL | 2 | RC6/2X18W/CFL | 2C0018E | 32 | 40 | 1.28 | 3200 | 4096 | 712.704 | NEW/13W/LED/RECESSED CAN | 32 |  |  | 1L013 | 13 | 0 | 3200 | 0.416 | 1331.2 | 0% | 0% | 0 | 1331.2 | 231.6288 | 481.0752 | 35K | 7479.3168 | 15.5471 | 6615.3168
23 | 2ND FLOOR HALL | 2 | RC6/2X18W/CFL | 2C0018E | 30 | 40 | 1.2 | 3200 | 3840 | 668.16 | NEW/13W/LED/RECESSED CAN | 30 |  |  | 1L013 | 13 | 0 | 3200 | 0.39 | 1248 | 0% | 0% | 0 | 1248 | 217.152 | 451.008 | 35K | 7011.8595 | 15.5471 | 6201.8595
24 | MAIN STAIRWELL | 2 | 18"DRUM/28W/FLOUR | 1C0028E | 6 | 30 | 0.18 | 3200 | 576 | 100.224 | KIT/DRUM_7W/LED/ | 6 |  |  | 1L007 | 7 | 0 | 3200 | 0.042 | 134.4 | 0% | 0% | 0 | 134.4 | 23.3856 | 76.8384 | 35K | 1274.6406 | 16.5886 | 1136.6406
25 | LIBRARY | 2 | TT/2F40W/BIAX/BASKET | 2F40BXE | 32 | 72 | 2.304 | 3200 | 7372.8 | 1282.8672 | NEW/TT/LED/20W/ | 32 |  |  | 1L020 | 20 | 0 | 3200 | 0.64 | 2048 | 0% | 0% | 0 | 2048 | 356.352 | 926.5152 | 35K | 9475.9865 | 10.2276 | 7811.9865
26 | LIBRARY | 2 | RC6/2X18W/CFL | 2C0018E | 5 | 40 | 0.2 | 3200 | 640 | 111.36 | NEW/13W/LED/RECESSED CAN | 5 |  |  | 1L013 | 13 | 0 | 3200 | 0.065 | 208 | 0% | 0% | 0 | 208 | 36.192 | 75.168 | 35K | 1168.6432 | 15.5471 | 1033.6432
27 | ROOM B208 | 2 | RC6/2X18W/CFL | 2C0018E | 1 | 40 | 0.04 | 3200 | 128 | 22.272 | NEW/13W/LED/RECESSED CAN | 1 |  |  | 1L013 | 13 | 0 | 3200 | 0.013 | 41.6 | 0% | 0% | 0 | 41.6 | 7.2384 | 15.0336 | 35K | 233.7286 | 15.5471 | 206.7286
28 | ROOM B209 | 2 | RC6/2X18W/CFL | 2C0018E | 1 | 40 | 0.04 | 3200 | 128 | 22.272 | NEW/13W/LED/RECESSED CAN | 1 |  |  | 1L013 | 13 | 0 | 3200 | 0.013 | 41.6 | 0% | 0% | 0 | 41.6 | 7.2384 | 15.0336 | 35K | 233.7286 | 15.5471 | 206.7286
29 | MENS B210 | 2 | RC6/2X18W/CFL | 2C0018E | 3 | 40 | 0.12 | 3200 | 384 | 66.816 | NEW/13W/LED/RECESSED CAN | 3 |  |  | 1L013 | 13 | 0 | 3200 | 0.039 | 124.8 | 0% | 0% | 0 | 124.8 | 21.7152 | 45.1008 | 35K | 701.1859 | 15.5471 | 620.1859
30 | WOMENS B211 | 2 | RC6/2X18W/CFL | 2C0018E | 3 | 40 | 0.12 | 3200 | 384 | 66.816 | NEW/13W/LED/RECESSED CAN | 3 |  |  | 1L013 | 13 | 0 | 3200 | 0.039 | 124.8 | 0% | 0% | 0 | 124.8 | 21.7152 | 45.1008 | 35K | 701.1859 | 15.5471 | 620.1859
31 | LINCOLN RM DOOR 11 STAIRS | 2 | TT/2FB31/E/9-CELL | 2F32SSE | 2 | 60 | 0.12 | 3200 | 384 | 66.816 | RB/TT/22W_2BAR/_KIT | 2 |  |  | 1L020 | 22 | 0 | 3200 | 0.044 | 140.8 | 0% | 0% | 0 | 140.8 | 24.4992 | 42.3168 | 35K | 403.5026 | 9.5353 | 327.5026
32 | LINCOLN RM DOOR 11 STAIRS | 2 | 18"DRUM/28W/FLOUR | 0 | 2 | 30 | 0.06 | 3200 | 192 | 33.408 | KIT/DRUM_7W/LED/ | 2 |  |  | 1L007 | 7 | 0 | 3200 | 0.014 | 44.8 | 0% | 0% | 0 | 44.8 | 7.7952 | 25.6128 | 35K | 424.8802 | 16.5886 | 378.8802
33 | BOYS ROOM B139 | 1 | RC6/2X18W/CFL | 2C0018E | 3 | 40 | 0.12 | 3200 | 384 | 66.816 | NEW/13W/LED/RECESSED CAN | 3 |  |  | 1L013 | 13 | 0 | 3200 | 0.039 | 124.8 | 0% | 0% | 0 | 124.8 | 21.7152 | 45.1008 | 35K | 701.1859 | 15.5471 | 620.1859
34 | GIRLS ROOM B140 | 1 | RC6/2X18W/CFL | 2C0018E | 3 | 40 | 0.12 | 3200 | 384 | 66.816 | NEW/13W/LED/RECESSED CAN | 3 |  |  | 1L013 | 13 | 0 | 3200 | 0.039 | 124.8 | 0% | 0% | 0 | 124.8 | 21.7152 | 45.1008 | 35K | 701.1859 | 15.5471 | 620.1859
35 | HALLWAY B140 | 1 | TT/2FB31/E/9-CELL | 2F32SSE | 1 | 60 | 0.06 | 3200 | 192 | 33.408 | RB/TT/22W_2BAR/_KIT | 1 |  |  | 1L020 | 22 | 0 | 3200 | 0.022 | 70.4 | 0% | 0% | 0 | 70.4 | 12.2496 | 21.1584 | 35K | 201.7513 | 9.5353 | 163.7513
36 | DOOR 6 | 1 | TT/2FB31/E/9-CELL | 2F32SSE | 1 | 60 | 0.06 | 3200 | 192 | 33.408 | RB/TT/22W_2BAR/_KIT | 1 |  |  | 1L020 | 22 | 0 | 3200 | 0.022 | 70.4 | 0% | 0% | 0 | 70.4 | 12.2496 | 21.1584 | 35K | 201.7513 | 9.5353 | 163.7513
37 | B128 STAFF RESTROOM | 1 | RC6/2X18W/CFL | 2C0018E | 1 | 40 | 0.04 | 3200 | 128 | 22.272 | NEW/13W/LED/RECESSED CAN | 1 |  |  | 1L013 | 13 | 0 | 3200 | 0.013 | 41.6 | 0% | 0% | 0 | 41.6 | 7.2384 | 15.0336 | 35K | 233.7286 | 15.5471 | 206.7286
38 | B127 STAFF RESTROOM | 1 | RC6/2X18W/CFL | 2C0018E | 1 | 40 | 0.04 | 3200 | 128 | 22.272 | NEW/13W/LED/RECESSED CAN | 1 |  |  | 1L013 | 13 | 0 | 3200 | 0.013 | 41.6 | 0% | 0% | 0 | 41.6 | 7.2384 | 15.0336 | 35K | 233.7286 | 15.5471 | 206.7286
39 | HALLWAY B127 | 1 | TT/2FB31/E/9-CELL | 2F32SSE | 3 | 60 | 0.18 | 3200 | 576 | 100.224 | RB/TT/22W_2BAR/_KIT | 3 |  |  | 1L020 | 22 | 0 | 3200 | 0.066 | 211.2 | 0% | 0% | 0 | 211.2 | 36.7488 | 63.4752 | 35K | 605.2539 | 9.5353 | 491.2539
40 | CAFÉ SERVING AREA | 1 | TT/2FB31/E/PRISMATIC | 2F32SSE | 9 | 60 | 0.54 | 3200 | 1728 | 300.672 | RB/TT/22W_2BAR/_KIT | 9 |  |  | 1L020 | 22 | 0 | 3200 | 0.198 | 633.6 | 0% | 0% | 0 | 633.6 | 110.2464 | 190.4256 | 35K | 1815.7616 | 9.5353 | 1473.7616
41 | CAFÉ | 1 | 18"DRUM/28W/FLOUR | 0 | 15 | 30 | 0.45 | 3200 | 1440 | 250.56 | KIT/DRUM_7W/LED/ | 15 |  |  | 1L007 | 7 | 0 | 3200 | 0.105 | 336 | 0% | 0% | 0 | 336 | 58.464 | 192.096 | 35K | 3186.6015 | 16.5886 | 2841.6015
42 | CAFÉ | 1 | CUSTOM/PEND/28W&3L/40W-BIAX | 3F40BXE + 30 | 14 | 132 | 1.848 | 3200 | 5913.6 | 1028.9664 | NA | 0 |  |  | NA | 132 | 0 | 3200 | 1.848 | 5913.6 | 0% | 0% | 0 | 5913.6 | 1028.9664 | 0 |  | 0 |  | 0
43 | BOYS ROOM B124 | 1 | RC6/2X18W/CFL | 2C0018E | 2 | 40 | 0.08 | 3200 | 256 | 44.544 | NEW/13W/LED/RECESSED CAN | 2 |  |  | 1L013 | 13 | 0 | 3200 | 0.026 | 83.2 | 0% | 0% | 0 | 83.2 | 14.4768 | 30.0672 | 35K | 467.4573 | 15.5471 | 413.4573
44 | GIRLS ROOM B123 | 1 | RC6/2X18W/CFL | 2C0018E | 2 | 40 | 0.08 | 3200 | 256 | 44.544 | NEW/13W/LED/RECESSED CAN | 2 |  |  | 1L013 | 13 | 0 | 3200 | 0.026 | 83.2 | 0% | 0% | 0 | 83.2 | 14.4768 | 30.0672 | 35K | 467.4573 | 15.5471 | 413.4573
45 | STAFF REST ROOM B115 | 1 | RC6/2X18W/CFL | 2C0018E | 1 | 40 | 0.04 | 3200 | 128 | 22.272 | NEW/13W/LED/RECESSED CAN | 1 |  |  | 1L013 | 13 | 0 | 3200 | 0.013 | 41.6 | 0% | 0% | 0 | 41.6 | 7.2384 | 15.0336 | 35K | 233.7286 | 15.5471 | 206.7286
46 | STAFF REST ROOM B114 | 1 | RC6/2X18W/CFL | 2C0018E | 1 | 40 | 0.04 | 3200 | 128 | 22.272 | NEW/13W/LED/RECESSED CAN | 1 |  |  | 1L013 | 13 | 0 | 3200 | 0.013 | 41.6 | 0% | 0% | 0 | 41.6 | 7.2384 | 15.0336 | 35K | 233.7286 | 15.5471 | 206.7286
47 | MAIN OFFICE B103 | 1 | TT/2FB31/E/9-CELL | 2F32SSE | 29 | 60 | 1.74 | 3200 | 5568 | 968.832 | RB/TT/32W_3BAR/_KIT | 29 |  |  | 1L032 | 32 | 0 | 3200 | 0.928 | 2969.6 | 0% | 0% | 0 | 2969.6 | 516.7104 | 452.1216 | 35K | 6625.7262 | 14.6547 | 5813.7262
48 | MAIN ENTRANCE | 1 | TT/2FB31/E/9-CELL | 2F32SSE | 8 | 60 | 0.48 | 3200 | 1536 | 267.264 | RB/TT/22W_2BAR/_KIT | 8 |  |  | 1L020 | 22 | 0 | 3200 | 0.176 | 563.2 | 0% | 0% | 0 | 563.2 | 97.9968 | 169.2672 | 35K | 1614.0103 | 9.5353 | 1310.0103
49 | MAIN HALL | 1 | RC6/2X18W/CFL | 2C0018E | 14 | 40 | 0.56 | 3200 | 1792 | 311.808 | NEW/13W/LED/RECESSED CAN | 14 |  |  | 1L013 | 13 | 0 | 3200 | 0.182 | 582.4 | 0% | 0% | 0 | 582.4 | 101.3376 | 210.4704 | 35K | 3272.2011 | 15.5471 | 2894.2011
50 | MAIN HALL | 1 | RC6/2X18W/CFL | 2C0018E | 5 | 40 | 0.2 | 3200 | 640 | 111.36 | NEW/13W/LED/RECESSED CAN | 5 |  |  | 1L013 | 13 | 0 | 3200 | 0.065 | 208 | 0% | 0% | 0 | 208 | 36.192 | 75.168 | 35K | 1168.6432 | 15.5471 | 1033.6432
51 | MAIN STAIRWELL | 1 | RC6/2X18W/CFL | 2C0018E | 4 | 40 | 0.16 | 3200 | 512 | 89.088 | NEW/13W/LED/RECESSED CAN | 4 |  |  | 1L013 | 13 | 0 | 3200 | 0.052 | 166.4 | 0% | 0% | 0 | 166.4 | 28.9536 | 60.1344 | 35K | 934.9146 | 15.5471 | 826.9146
52 | MAIN STAIRWELL | 1 | RC6/2X18W/CFL | 2C0018E | 4 | 40 | 0.16 | 3200 | 512 | 89.088 | NEW/13W/LED/RECESSED CAN | 4 |  |  | 1L013 | 13 | 0 | 3200 | 0.052 | 166.4 | 0% | 0% | 0 | 166.4 | 28.9536 | 60.1344 | 35K | 934.9146 | 15.5471 | 826.9146
53 | NURSE'S OFC | 1 | TT/2FB31/E/9-CELL | 2F32SSE | 8 | 60 | 0.48 | 3200 | 1536 | 267.264 | RB/TT/22W_2BAR/_KIT | 8 |  |  | 1L020 | 22 | 0 | 3200 | 0.176 | 563.2 | 0% | 0% | 0 | 563.2 | 97.9968 | 169.2672 | 35K | 1614.0103 | 9.5353 | 1310.0103
54 | NURSE'S OFC RESTROOM | 1 | RC6/2X18W/CFL | 2C0018E | 1 | 40 | 0.04 | 3200 | 128 | 22.272 | NEW/13W/LED/RECESSED CAN | 1 |  |  | 1L013 | 13 | 0 | 3200 | 0.013 | 41.6 | 0% | 0% | 0 | 41.6 | 7.2384 | 15.0336 | 35K | 233.7286 | 15.5471 | 206.7286
59 | SITE LIGHTING | OUT | HALF-MOONS/42W/CFL | 1C0042E | 20 | 48 | 0.96 | 4380 | 4204.8 | 731.6352 | KIT/DRUM_12W/LED/ | 20 |  |  | 1L012 | 12 | 0 | 4380 | 0.24 | 1051.2 | 0% | 0% | 0 | 1051.2 | 182.9088 | 548.7264 | 5k | 4391.3195 | 8.0027 | 3671.3195
[5 empty] | 410 |  | 26.442 |  | 103691.68 | 13855.1328 |  | 367 | [6 empty] | 12.94 | 35283.2 |  |  |  | 35448.32 | 6168.0077 | 7687.1251 |  | 93372.992 | 12.1467 | 79870.992
| Annual Savings: |  | 7687.1251 | [6 empty] | ECM Qty | Fixture Legend | [5 empty] | Color | Lumens | Manufacturer |  | Part Number
| kW Reduced: |  | 13.502 | [6 empty] | 36 | KIT/DRUM_12W/LED/ | LED Drum Retrofit kit |  |  |  |  | 30-35K | 1500 | RemPhos |  | RPT-LEDCR-1600LM-3000K
| kWh Savings: |  | 68243.36 | [6 empty] | 25 | KIT/DRUM_7W/LED/ | LED Drum Retrofit kit |  |  |  |  | 30-35K | 850 | RemPhos |  | RPT-LEDCR-900LM-3000K
[10 empty] | 189 | NEW/13W/LED/RECESSED CAN | New LED 6" Recessed Can |  |  |  |  | 35K | 900 | Sylvania |  | LED/RT5/6/HO//900/835
[10 empty] | 12 | NEW/LED/86W/SEN/STEP-DIM | New LED High Bay with integrated sensor |  |  |  |  | 4K | 11738 | Flex Lusio Essentials |  | ES3P-A-4MS-40-WIDE-FR-LV-CRM-10V-OCC40-CORDN-EMBN-OPTN
[10 empty] | 32 | NEW/TT/LED/20W/ | New LED 2x2 troffer |  |  |  |  | 35K | 2213 | Lithonia Lighting |  | 2FSL2 20L EZ1 LP835
[10 empty] | 44 | RB/TT/22W_2BAR/_KIT | 2x2 Troffer, 2 Bar LED Retrofit kit |  |  |  |  | 35K | 2300 | Litetronics |  | RF-22-U-Q-T2-35
[10 empty] | 29 | RB/TT/32W_3BAR/_KIT | 2x2 Troffer, 3 Bar LED Retrofit kit |  |  |  |  | 35K | 3600 | Litetronics |  | RF-32-U-Q-T2-35